承認書

Specification  For  Approval

| COMPANY NAME | 朱星贸易 |
| --- | --- |
| CUSTOMER P/N |  |
| PRODUCT NAME | AC/DC ADAPTER |
| PARTS P/N | CP1250 |
| DATE | 2009-8-4 |

| APPROVED BY | CHECKED BY | PREPARED BY | CUSTOMER APPROVAL SIGNATURE |
| --- | --- | --- | --- |

寶三電子有限公司

POWSUN CO.,LTD.

一厂：

工厂地址：广东省东莞市清溪镇渔梁围朱屋村

TEL：（0769）86814578

FAX：（0769）86814576

二厂：

工厂地址：广东东莞清溪镇长山头村康怡路180号

TEL：（0769）86814698

FAX：（0769）86814697

http://www.powsun.com

E-mail:wyj@powsun.com

TABLE OF CONTENTS

- FEATURE----------------------------------------------------------------------------------------------  2

- INPUT---------------------------------------------------------------------------------------------------  2

INPUT VOLTAGE-------------------------------------------------------------------------------------  2

INPUT FREQUENCY---------------------------------------------------------------------------------  2

INPUT CURRENT-------------------------------------------------------------------------------------  2

INRUSH CURRENT----------------------------------------------------------------------------------  2

EFFICIENCY-------------------------------------------------------------------------------------------  2

INPUT POWER DISSIPATION--------------------------------------------------------------------   2

- OUTPUT------------------------------------------------------------------------------------------------  2

OUTPUT VOLTAGE----------------------------------------------------------------------------------  2

OUTPUT CURRENT----------------------------------------------------------------------------------  2

REGULATION-----------------------------------------------------------------------------------------  2

RIPPLE & NOISE--------------------------------------------------------------------------------------  2

TOTAL POWER----------------------------------------------------------------------------------------  2

- PROTECTION----------------------------------------------------------------------------------------  2

OVER VOLTAGE PROTECTION-------------------------------------------------------------------  2

SHORT CIRCUIT PROTECTION-------------------------------------------------------------------  2

OVER POWER PROTECTION----------------------------------------------------------------------  2

- SAFETY AND EMI REQUIREMENT-----------------------------------------------------------  3

SAFETY REQUIREMENT---------------------------------------------------------------------------  3

EMI REQUIREMENT---------------------------------------------------------------------------------  3

LEAKAGE CURRENT--------------------------------------------------------------------------------  3

- OPERATION & ENVIRONMENT PERFORMANCE---------------------------------------  3

TEMPERATURE RANGE----------------------------------------------------------------------------  3

HUMIDITY RANGE(NON CONDENSING)------------------------------------------------------  3

- M.T.B.F--------------------------------------------------------------------------------------------------  3

- SAMPLE TEST REPORT-----------------------------------------------------------------------  4、5

- OUTLINE DRAWING-----------------------------------------------------------------------------------6

1. FEATURE:

 INPUT       :UNIVERSAL  100-240 Vac/47-63  Hz  INPUT,  W I THOUT  ANY  SLIDE  SW I TCH

 OUTPUT    :+12V / 0-5A

 DIMENSION :117(D)*64(W)*35(H)

 EFFICIENCY :82% TYPICAL

 SAFETY     : UL/BSMI/CB/CE/TUV/C-Tick/DOFT/PSE/CCC/KE

 EMI          :CISPR  22 / FCC /VCCI  CLASS  B; CONDUCTED & RADIATED  MEETED

 HIGH  FREQUENCY  DESIGN,  LESS  POWER  CONSUMPTION

 OVER VOLTAGE  PROTECTION,  SHORT  CIRCU ITED  PROTECTION,  OVER  POWER  PROTECTION

 CAN BE USED AT TEL COMMUNICATION, COMPUTER, INDUSTRIAL CONTORLLER & OA SYSTEM

2. INPUT:

| 2. 1 VOLTAGE | UNIVERSAL 100~240Vac,SINGLE PHASE |
| --- | --- |
| 2. 2 FREQUENCY | 47HZ~63HZ |
| 2. 3 CURRENT | 1.8A Max |
| 2. 4 INRUSH CURRENT | 42A Max/100Vac;84A Max/240Vac (COLD STABT AT 25℃ FULL LOAD) |
| 2. 5 EFFICIENCY | 82% TYPICAL (AT NOMINAL LINE VOLTAGE FULL LOAD) |
| 2. 6 INPUT POWER DISSIPATION | UNDER 0.5W < ZERO LOAD 115V/60HZ INPUT |
|  | UNDER 0.5W < ZERO LOAD 230V/50HZ INPUT |

3. OUTPUT:

| 3. 1 DC OUTPUT | VOLTAGE | +12.00V |
| --- | --- | --- |
|  | CURRENT | 5.0A Max |
|  | REGULATION | 11.40V Min~12.00V Typ.~12.60V Max |
|  | RIPPLE & NOISE | 120mV Max |
|  | TOTAL POWER | 60W Max |

NOTE: FOR RIPPLE & NOISE MEASUREMENT, USE A 20MHZ BAND WIDTH FREQUENCY OSCILLOSCOPF, AND ADD A 0.1uF MULTILAYER CAP.  AND A LOW ESR ELECTROLYTICCAP. (10uF)  AT OUTPUT CONNECTOR TERMINALS. (AT NOMINAL LINE VOLTAGE FULL LOAD)

4. PROTECTION:

| 4. 1 OVER VOLTAGE PROTECTION | V out*(110%-140%) |
| --- | --- |
| 4. 2 SHORT CIRCUIT PROTECTION | AUTOMATIC RECOVERY AFTER SHORT-CIRCUIT FAULT REMOVED |
| 4. 3 OVER POWER PROTECTION | THE ADAPTER PROVIDE PROTECTION AT 110-140% OF RATED OUTPUT POWER |

NOTE: WHEN PROTECTION CIRCUIT IS WORKING THE POWER SUPPLY WILL SHUTDOWN, ONCE THE ABNORMAL CONDITIONS ARE REMOVED. THE POWER SUPPLY WILL RESTART AUTOMATICALLY.

5. SAFETY AND EMI REQUIREMENT:

5.1 SAFETY REQUIREMENT

a. SAFETY               : UL/BSMI/CB/CE/TUV/C-Tick/DOFT/PSE/CCC/KE

b. DIELECTRIC STRENGTH :10mA Max. CUT OFF CURRENT

| (1):PRIMARY TO SECONDARY | : 1500Vac FOR 1 MINUTE |
| --- | --- |
| (2):PRIMARY TO FRAME GROUND | : 1500Vac FOR 1 MINUTE |

c. INSULAION RESISTANCE:

| (1):PRIMARY TO SECONDARY | : 10 M OHMS FOR 500Vdc |
| --- | --- |
| (2):PRIMARY TO FRAME GROUND | : 10 M OHMS FOR 500Vdc |

5.2 EMI  REQUIREMENT  MEET  CISPR 22/FCC/VCC1, CLASS B

5.3 LEAKAGE  CURRENT  LESS  THAN 3.5mA

6.OPERATION & ENVIRONMENT PERFORMANCE:

6.1 TEMPERATURE RANGE

| OPERATING | 0℃ ~ +40℃ |
| --- | --- |
| STORAGE | -40℃ ~+70℃ |

6.2 HUMIDITY RANGE (NON CONDENSING)

| OPERATING | 10% ~ 90% RH |
| --- | --- |
| STORAGE | 5% ~ 95% RH |

6.3 COOLING                 SHOULD OPERATE WITHOUT FAN

7.M.T.B.F.:                50000 HOURS Min ; 40℃ SEE CONDITION

TEST REPORT

( I ). LINE REGULATION TEST

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 90Vac / 50% load | 11.40~12.60V | 12.07V |
| 115Vac / 50% load | 11.40~12.60V | 12.07V |
| 132Vac / 50% load | 11.40~12.60V | 12.07V |
| 180Vac / 50% load | 11.40~12.60V | 12.07V |
| 230Vac / 50% load | 11.40~12.60V | 12.07V |
| 264Vac / 50% load | 11.40~12.60V | 12.07V |

(II). EFFICENCY TEST

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | 84% Typical | 84.3% |
| 230Vac / 100% load | 84% Typical | 84.1% |

(III). LOAD REGULATION TEST

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 0% load | 11.40~12.60V | 12.43V |
| 115Vac / 50% load | 11.40~12.60V | 12.07V |
| 115Vac / 100% load | 11.40~12.60V | 11.69V |
| 230Vac / 0% load | 11.40~12.60V | 12.43V |
| 230Vac / 50% load | 11.40~12.60V | 12.07V |
| 230Vac / 100% load | 11.40~12.60V | 11.69V |

(IV).RIPPLE & NOISE TEST

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | 120mV Max | 110mV |
| 230Vac / 100% load | 120mV Max | 90mV |

(VI). OVER VOLTAGE PROTECTION

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | Vout*(110%~140%) | 118% |
| 230Vac / 100% load | Vout*(110%~140%) | 125% |

(VII). RISE TIME

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | 50mS Max | OK |
| 230Vac / 100% load | 50mS Max | OK |

(VIII). OVER CURRENT PROTECTION

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | Iout*(110%~140%) | 120% |
| 230Vac / 100% load | Iout*(110%~140%) | 122% |

(IX). SHORT CIRCUIT PROTECTION

Test result:

| Test condition | Spec. | Reading |
| --- | --- | --- |
| 115Vac / 100% load | Under 1W | OK |
| 230Vac / 100% load | Under 1W | OK |